## Natural Vent Calculation
Project Ref:
Project Name: |  |  |  | Key
Customer: |  |  |  |  | Cells requiring input
Engineer: |  |  |  |  | Calculated cells
Date:
Floor Area m2 | 0 | m2
| Column 1 |  | Column 2 |  | Column 3
| Free area of openings required to meet Document B & F (m2) |  | Free area of openings required to meet Document B only (m2) |  | Free area of openings proposed for this project (m2) |  | Meets requirement for Document F and B | Meets requirement for Document B only
Opposing Side A | 0 | m2 (Min) | 0 | m2 (Min) | 0 | m2 | Yes | Yes
Opposing Side B | 0 | m2 (Min) | 0 | m2 (Min) | 0 | m2 | Yes | Yes
Additional area required (only required if the 2no. Opposing sides do not meet the total requirement) - anywhere with car park | 0 | m2 | 0 | m2 | 0 | m2
Total Required/Proposed Area | 0 | m2 | 0 | m2 | 0 | m2 | Yes | Yes
Total Required/Proposed % | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
[7 empty] | FALSE | FALSE
Results: | FALSE | Natural Ventilation Provision does not meet requirements
| TRUE | Natural Ventilation Provision satisfies requirements
Note 1: No ventilation will be required if the car park openings meet the minimum requirements detailed within Column 1 for the opposing sides and the total area - openings are to be provided through opposing walls and cannot be vertical through the soffit to meet the requirements of ADF.
Note 2: Supplementary ventilation will be required with the use of jet fans only if the car park openings meet only the minimum requirements detailed within Column 2 for the opposing sides and the total area (the system is to limit the concentration of CO to below 25ppm averaged over an 8 hour period) - openings can be provided vertically through the soffit to meet the requirements of ADB, however the cross ventilation must be provided through two opposing walls
Estimated Number of CO detectors | 0 |  | [Based on CO detector with effective coverage area of 400m2] |  |  |  |  | 0
Estimated Number of Jet Fans | 0 |  | [Based on 355mm dia Jetfan with effective coverage area 450m2] |  |  |  |  | 0
355mm Jetfan mounting depth = 455mm
Note: Final quantity and placement of Jetfans to be determined by CFD modelling